## Specifications - Terms Matrix
| Appendix A | Bidder: _________________________________
| RFP #DS011020 | Date: _____________________________________
Specifications - Terms Matrix
Instructions: Please state whether you acknowledge, meet, or exceed standard for each RFP section below as appropriate (Standard RFP Requirements, Scope Requirements, Instructions to Prposers and Standard Contract Terms and Conditions). You must list all exceptions taken next to the appropriate section or accept all University terms as is. Several standard provisions are required by law and taking exceptions to such provisions may delay the contracting process or cause a rejection of your proposal. You may attach additonal sheets as necessary to provide a complete response for any item. Please include the Section number for reference.
Standard RFP Requirements
Section | Description | Acknowledge (Acknowledge /No): | Exceptions Taken:
3.2 | Bid Understanding
3.3 | Rendering of Products / Services
3.4 | Product Requirements
3.5 | Expiration of Bids
3.6 | ITB Acceptance/Rejection
3.7 | Modified Proposals
3.8 | Pricing - Appendix B
3.9 | Additional Costs
3.1 | Sales Tax
3.11 | References
3.12 | Good Faith Negotiation
3.13 | Incorporation of Bid
3.14 | Bid Preparation
3.15 | Minor Defects
3.16 | Notification of Bid Status
3.17 | Debriefing
3.18 | Exceptions
Scope of Work / Specifications
Section | Overview | Acknowledge (Acknowledgeor No): | Exceptions Taken:
4.1 | Basis of design is Hardwall Modular Cleanroom by Terra Universal, Inc., 800 S. Raymond Ave., Fullerton, CA 92831 (7145786000). Acceptable comparable products include those manufactured by Liberty Industries Inc., 133 Commerce Street, East Berlin, CT 06023 (8008285656), and AES Clean Technology, 422 Stump Road, Montgomery, PA 18936 (2153936810).
Requests for substitutions will be considered.
Drawings are provided in Attachment 3 are for reference only. They are based on the Terra equipment
Standards:
4.2.1 | ISO 14644-1: 2015 Cleanrooms and associated controlled environments -Part 1: Classification of air cleanliness by particle concentration.
4.2.2 | Underwriter's Laboratory File E472687: Including all high-voltage Modular Cleanroom electrical components integrated into power distribution system
4.3 | Manufacturer's Qualifications: Firm that has produced modular cleanrooms for not less than 10 years, with not less than 50 similar projects that have been in successful use for not less than 5 years.
Minimum Specifications
4.4.1 | Cleanroom; Hardwall, Modular, Static-Dissipative PVC Panels, Powder-Coated Steel Frame
4.4.2 | Dimensions: 18' x 16' x 7'-6"H (Internal height from floor to filter face)
4.4.3 | Class 10,000
4.4.4 | Indicate if Seismic analysis is available (on Appendix A – Point-by-Point response)
Components
4.5.1 | HEPA filter units to direct a continuous flow of air through the enclosure.
4.5.2 | Frame Components: Cleanroom is supported by a rigid frame consisting of powder­ coated 2" x 2" steel upright members and horizontal cross members. Powder-coated joists supported by the frame form 2' x 4' ceiling grids that accommodate the interchangeable ceiling modules.
4.5.3 | Ceiling modules rest against the ceiling grid frame to form a tight seal along the perimeters.
4.5.4 | Side Panels: Rigid side panels of the Modular Cleanroom are made of lightweight, transparent static dissipative PVC.
4.5.5 | The wall panels are attached to the support frame with stainless steel braces and fasteners.
4.5.6 | Fan Filter Unit; WhisperFlow, RSR, 2' x 4', HEPA, 120 V, Powder-Coated Steel 4.5.6.1 Challenge Port; for Fan/Filter Unit 4.5.6.2 Filter Replacement Alarm System; for Fan Filter Unit, Audible Alert, Manual Override, Stainless Steel, 120V 4.5.6.3 Night Service Switch
4.5.7 | Light Panels: LED light panels are compatible with ISO 7 cleanliness standards and are mounted on the ceiling grid to effectively illuminate the work area without interfering with the controlled air stream. Each fixture produces 5000 lumens at a color temperature of 4000K. Each light panel is controlled by the power supply unit. l l 5VAC/60 Hz, l.5A each.
4.5.8 | Ceiling Panel for Modular Cleanrooms; 2' x 4', Polypropylene
4.5.9 | Power Distribution Module, Primary, FFU/Light, 120V, UL Listed
4.5.10 | Control Panel w/OSI; for Hardwall CR, External-Mount Panel, Night Switch,120V
4.5.11 | Power Distribution Module, Duplex, 120V, UL Listed
4.5.12 | Door; Static-Dissipative, Sliding, for Hardwall Cleanroom
Responsibilities of the Vendor
4.6.1 | Assess the building and final location for the equipment to determine any limitations that may affect the delivery of the components
4.6.2 | Field measure the laboratory space
4.6.3 | Provide Shop Drawings prior to proceeding with sales order.
4.6.4 | Compliance with OSHA 10
4.6.5 | Perform all work on campus during normal workday hours Mon‐Fri only
4.6.6 | University Parking permits are required and to be purchased by/at Vendors expense.
4.6.7 | Site required to be kept organized and clean during the work and broom clean at end of each workday and end of project
4.6.8 | All tools, material handling equipment, cords, etc. are the vendor’s responsibility to provide to do the work.
4.7 | Responsibilities of the University
Submittals
4.8.1 | PROVIDE COMPLETE SPECIFICATIONS INCLUDING FINISHES MEASUREMENTS AND AIRFLOW REQUIREMENTS FOR CEILING MOUNTED COMPONENTS. Options including, but not limited to, access doors, air conditioning, air locks and antechambers, air flow and pressure gauges, and furnishings (Submit as Exhibit 1)
4.8.2 | Manufacturer's installation instructions. (Submit as Exhibit 2)
4.8.3 | Provide UL Listing Declaration for cleanroom electrical system. (Submit as Exhibit 3)
4.8.4 | Operation and Maintenance Manual: Submit complete instruction and maintenance manual for cleanroom that includes sequential operating instructions, routine preventative maintenance instructions, and complete schematic drawings of rooms. (Submit as Exhibit4)
4.8.5 | Warranty: Provide manufacturer's written one-year warranty for a period of one year against defects. Manufacturer shall agree to repair or replace items proven to be defective (Submit as Exhibit 5)
Standard Contract Terms and Conditions
Section |  | Acknowledge (Acknowledge or No): | Exceptions Taken:
7.1 | Contract Status
7.2 | Contract Format
7.3 | Contract Modification
7.4 | Contract Assignment or Subcontract
7.5 | Notification of Selected Firm
7.6 | Contract Commencement
7.7 | Ownership of Subsquent Samples
7.8 | Independent Price Determination
7.9 | Professional Time and Expense
7.1 | Sales Tax Exemption
7.11 | Non-Appropriation of Funds
7.12 | Indemnification Requirements
7.13 | Liens
7.14 | Choice of Law and Venue
7.15 | Actions of Proposer
7.16 | Award
7.17 | Payments under a Contract Award
7.18 | Evluation of Performance
7.19 | Business Relationship Affidavit
7.2 | Conflict of Interest
7.21 | Equal Employment Opportunity Requirements
7.22 | Federal, State and Local Taxes, Licenses and Permits
7.23 | Waiver of Rights
7.24 | Prior Course of Dealings
7.25 | Warranty
7.26 | Proposer Personnel
7.27 | Information Provided by the University
7.28 | Responsibilities of the Proposer
7.29 | Repairs to Property Damage
7.3 | Access Management Plan
7.31 | Insurance Requirements
7.32 | License
7.33 | OSHA Compliance
7.34 | Advertising/Sponsorship Opportunities
7.35 | Licensed Merchandise
7.36 | Intellectual Property
7.37 | Confidential Information
7.38 | Responsibility of Those Performing Work
7.39 | Freedom of Information
7.4 | Mandatory Affidavits
7.41 | Joint Ventures
7.42 | Executive Orders of the Governor
7.43 | Equal Opportunity Employer
7.44 | Ethics and Compliance Reporting/Whistleblower Protection
7.45 | State Elections Enforcement Commission Requirements
7.46 | Nondiscrimination Warranties
7.47 | On-Site Accommodations
7.48 | Termination for Cause
7.49 | Termination for Convenience
7.5 | Corporate Social Responsibility
Standard Contract Terms & Conditions
| Section | Acknowledge (Acknowledge or No): | Exceptions Taken:
Attachment 2 - Gov. Rell Ethics Memo